## Sheet1 (2)
Jignesh.Parmar, www.electricalnotes.wordpress.com
CALCULATE MOTOR-PUMP SIZE |  |  |  | CALCULATE MOTOR-PUMP SIZE
:Pump Detail:
Static Suction Head: (h1) | 0 | Meter |  | Suction Pressure:(Ps) | 0.04 | kg/cm2
Static Discharge Head: (h2) | 50 | Meter |  | Discharge Pressure:(Pd) | 9 | kg/cm2 |  | 1 | liter
Is Pump Inlet Diameter equal to Outlet Diameter: |  |  |  | Volumetric Flow:(Q) | 150 | m3/jam |  |  | m3
Enter Pump Inlet Diameter: | 0.0127 | Meter |  | Specific Gravity:(SG) | 1 |  |  | 1 | min
Enter Pump Outlet Diameter: | 0.0127 | Meter |  | Gravity of Fluid:(g) | 9.8 | m/s2 |  |  | sec
Density of Liquid: (D) | 1000 | Kg/m3 |  | Pump Efficiency:(η) | 80%
Required Amount of Liquid at perticular Height | 900 |  | 0.9
Required Time for getting Liquid at perticular Height | 1 |  | 60 | Differential Pressure: | 8.96 | kg/cm2 |  | 2 | Yes
Flow Rate: (Q) | 0.015 | M3/Sec |  | Differential Head: | 89.6 | Meter |  |  | No
Inlet Velocity: (v1) | 118.4716 | M3/Sec |  | Required Differential Head:(H) | 91.392 | Meter
Outlet Velocity: (v2) | 118.4716 | M3/Sec
Velocity Head Inlet: (Vhi) | 715.3677 | Meter |  | Water Head Pressure (WHP): | 37.3184 | Kw | WHP=(SGxgxQxH)/3600
Velocity Head Outlet: (Vho) | 715.3677 | Meter |  | Pump's Brake Horse Power (BHP): | 46.648 | Kw | BHP=WHPxn
Difference in Velocity Head: (h3) | 0 | Meter |  | Safety Margin | 1.15
Total Head: | 50 | Meter
Frction Loass in Pipe | 30% |  |  | Required Motor Size: | 53.6452 | Kw | 72 HP
Actual Total Head (After Friction Losses): (H) | 65 | Meter
Pump Hydraulic Power: (ph) | 9.6233 | Kw
Pump Efficiency: (nP) | 80%
Motor/ Pump Shaft Power: (ps) | 12.0291 | Kw
Motor Efficiency: (nM) | 90%
Safety Margin (As per Americal Petroleum Institute (API): | 1
Required Motor Size: | 13.3656 | Kw | 18 HP
Liquid | Tem(°C) | Density(Kg/m3)
Acetic Acid | 25 | 1049
Acetone | 25 | 784.6
Acetonitrile | 20 | 782
Alcohol, ethyl (ethanol) | 25 | 785.1
Alcohol, methyl (methanol) | 25 | 786.5
Alcohol, propyl | 25 | 800
Ammonia (aqua) | 25 | 823.5
Aniline | 25 | 1019
Automobile oils | 15 | 880 - 940 |  | 0.0127 | 54
Beer (varies) | 10 | 1010 |  | 0.00635
Benzene | 25 | 873.8
Benzil | 15 | 1230
Brine | 15 | 1230
Bromine | 25 | 3120
Butyric Acid | 20 | 959
Butane | 25 | 599
n-Butyl Acetate | 20 | 880
n-Butyl Alcohol | 20 | 810
n-Butylhloride | 20 | 886
Caproic acid | 25 | 921
Carbolic acid | 15 | 956
Carbon disulfide | 25 | 1261
Carbon tetrachloride | 25 | 1584
Carene | 25 | 857
Castor oil | 25 | 956.1
Chloride | 25 | 1560
Chlorobenzene | 20 | 1106
Chloroform | 20 | 1489
Chloroform | 25 | 1465
Citric acid | 25 | 1660
Coconut oil | 15 | 924
Cotton seed oil | 15 | 926
Cresol | 25 | 1024
Creosote | 15 | 1067
Crude oil, 48o API | 60oF | 790
Crude oil, 40o API | 60oF | 825
Crude oil, 35.6o API | 60oF | 847
Crude oil, 32.6o API | 60oF | 862
Crude oil,alifornia | 60oF | 915
Crude oil, Mexican | 60oF | 973
Crude oil, Texas | 60oF | 873
Cumene | 25 | 860
Cyclohexane | 20 | 779
Cyclopentane | 20 | 745
Decane | 25 | 726.3
Diesel fuel oil 20 to 60 | 15 | 820 - 950
Diethyl ether | 20 | 714
o-Dichlorobenzene | 20 | 1306
Dichloromethane | 20 | 1326
Diethylene glycol | 15 | 1120
Dichloromethane | 20 | 1326
Dimethyl Acetamide | 20 | 942
N,N-Dimethylformamide | 20 | 949
Dimethyl Sulfoxide | 20 | 1100
Dodecane | 25 | 754.6
Ethane | -89 | 570
Ether | 25 | 713.5
Ethylamine | 16 | 681
Ethyl Acetate | 20 | 901
Ethyl Alcohol | 20 | 789
Ethyl Ether | 20 | 713
Ethylene Dichloride | 20 | 1253
Ethylene glycol | 25 | 1097
Freon (Fluorine) refrigerant R-11 | 25 | 1476
Fluorine refrigerant R-12 | 25 | 1311
Fluorine refrigerant R-22 | 25 | 1194
Formaldehyde | 45 | 812
Formic acid 10%oncentration | 20 | 1025
Formic acid 80%oncentration | 20 | 1221
Freon - 11 | 21 | 1490
Freon - 21 | 21 | 1370
Fuel oil | 60oF | 890
Furan | 25 | 1416
Furforol | 25 | 1155
Gasoline, natural | 60oF | 711
Gasoline, Vehicle | 60oF | 737
Gas oils | 60oF | 890
Glucose | 60oF | 1350 - 1440
Glycerine | 25 | 1259
Glycerol | 25 | 1126
Heating oil | 20 | 920
Heptane | 25 | 679.5
Hexane | 25 | 654.8
Hexanol | 25 | 811
Hexene | 25 | 671
Hydrazine | 25 | 795
Iodine | 25 | 4927
Ionene | 25 | 932
Isobutyl Alcohol | 20 | 802
Iso-Octane | 20 | 692
Isopropyl Alcohol | 20 | 785
Isopropyl Myristate | 20 | 853
Kerosene | 60oF | 820.1
Linolenic Acid | 25 | 897
Linseed oil | 25 | 929.1
Machine oil | 20 | 910
Mercury |  | 13590
Methane | -164 | 465
Methanol | 20 | 791
Methyl Isoamyl Ketone | 20 | 888
Methyl Isobutyl Ketone | 20 | 801
Methyl n-Propyl Ketone | 20 | 808
Methyl t-Butyl Ether | 20 | 741
N-Methylpyrrolidone | 20 | 1030
Methyl Ethyl Ketone | 20 | 805
Milk | 15 | 1020 - 1050
Naphtha | 15 | 665
Naphtha, wood | 25 | 960
Napthalene | 25 | 820
Nitric acid | 0 | 1560
Ocimene | 25 | 798
Octane | 15 | 698.6
Oil of resin | 20 | 940
Oil of turpentine | 20 | 870
Oil, lubricating | 20 | 900
Olive oil | 20 | 800 - 920
Oxygen (liquid) | -183 | 1140
Paraffin |  | 800
Palmitic Acid | 25 | 851
Pentane | 20 | 626
Pentane | 25 | 625
Perchlor ethylene | 20 | 1620
Petroleum Ether | 20 | 640
Petrol, natural | 60oF | 711
Petrol, Vehicle | 60oF | 737
Phenol | 25 | 1072
Phosgene | 0 | 1378
Phytadiene | 25 | 823
Pinene | 25 | 857
Propane | -40 | 493.5
Propane, R-290 | 25 | 494
Propanol | 25 | 804
Propylenearbonate | 20 | 1201
Propylene | 25 | 514.4
Propylene glycol | 25 | 965.3
Pyridine | 25 | 979
Pyrrole | 25 | 966
Rape seed oil | 20 | 920
Resorcinol | 25 | 1269
Rosin oil | 15 | 980
Sea water | 25 | 1025
Silane | 25 | 718
Silicone oil |  | 760
Sodium Hydroxide (caustic soda) | 15 | 1250
Sorbaldehyde | 25 | 895
Soya bean oil | 15 | 924 - 928
Stearic Acid | 25 | 891
Sulfuric Acid 95%onc. | 20 | 1839
Sulfurus acid | -20 | 1490
Sugar solution 68 brix | 15 | 1338
Sunflower oil | 20 | 920
Styrene | 25 | 903
Terpinene | 25 | 847
Tetrahydrofuran | 20 | 888
Toluene | 20 | 867
Trichlor ethylene | 20 | 1470
Triethylamine | 20 | 728
Trifluoroacetic Acid | 20 | 1489
Turpentine | 25 | 868.2
Water, heavy | 11.6 | 1105
Water - pure | 4 | 1000
Water - sea | 77oF | 1022
Whale oil | 15 | 925
o-Xylene | 20 | 880
Note on D6: vertical distance from source of reservoir(Vessale) to pump( +ve if source below pump, -ve if source above pump)
Note on D7: vertical distance from pump to surface of delivery reservoir / vessel
Note on M19: SAFETY MARGIN: Up to 25 HP(18.7 Kw) =1.25 30HP (22.4 Kw) to 52.2 Kw =1.15 Above 100 HP (74.6 Kw) = 1.10
Note on D27: SAFETY MARGIN: Up to 25 HP(18.7 Kw) =1.25 30HP (22.4 Kw) to 52.2 Kw =1.15 Above 100 HP (74.6 Kw) = 1.10